## Sheet1
Unit, etc. | Type number | No. of units | Quiescent (normal) |  | Alarm (activated) |  | Misc. | Comments
|  |  | à mA | Sum. mA | à mA | Sum. mA |  | Data shall be written in yellow cells only.
C.i.e.
EBL128 | 4550 | 1 | 109 | 109 | 125 | 125 |  | No. of units is always = 1. CAN NOT BE CHANGED!
RS485 transceiver component | 4552 | 0 | 14 | 0 | 14 | 0 |  | No. of units 0 or 1. For Display Units 1736, 1826 & 1828.
Web-server | 1588 | 0 | [5 empty] | No. of units 0 or 1. Current consumption will be aut. added below.
8 zones expansion board | 4580 | 0 | 22.2 | 0 | 22.2 | 0 |  | No. of units 0 or 1-2.
Zone line inputs used on 4580 board(s) |  | 0 | 3.5 | 0 | 12 | 0 |  | 4580: For each used zone line input 3,5/12 mA will be added in quiescent/alarm state.
8 relays expansion board | 4581 | 0 | 15 | 0 | 15 | 0 |  | No. of units 0 or 1-2.
Fuse for expansion boards: 500 mA.
Number of expansion boards |  | 0 | [5 empty] | NOTE! 4580+4581: max. 4.
Output S0 |  |  |  | 0 |  | 0 | Max. 500 mA | Normally low = high when activated; Normally high = low when activated
Output S1 |  |  |  | 0 |  | 0 | Max. 200 mA | Normally low = high when activated; Normally high = low when activated
24 V for external equipment / D.U. |  |  |  | 0 |  | 0 | Max. 500 mA | External equipment, e.g. Display Units 1736, 1826 & 1828.
24 V for Web-server 1588 |  |  | 65 | 0 | 65 | 0 |  | Web-server current consumption is added automatically.
24 V for routing equipment |  |  |  | 0 |  | 0 | Max. 200 mA
Display Units (D.U.): | [7 empty] | NOTE! Optional RS485 transceiver component 4552 required.
Ext. Presentation Unit | 1728 | 0 | 26 | 0 | 49 | 0 |  | No. of units 0 or 1-4. NOTE! The printer in 1826 will only print if the door is open and if there are fire alarms shown in the display.
Alert Annunciation Unit | 1736 | 0 | 26 | 0 | 42 | 0
External FBP (metal) excl. printer | 1826 | 0 | 26 | 0 | 49 | 0
External FBP (metal) incl. printer | 1826 | 0 | 30 | 0 | 210 | 0
External FBP | 1828 | 0 | 26 | 0 | 49 | 0
C.i.e. current consumption. (mA) |  |  |  | 109 |  | 125 |  | Regarding COM loop units, see below.
COM loop cable resistance (ohm/km) | [6 empty] | 24.5 | Resistance (ohm/km) according to the cable manufacturer's data sheet.
COM loop units
Analog smoke detector | 4301 | 0 | 0.3 | 0 | 0.3 | 0 |  | On the COM loop will max. 5 internal LEDs be turned on even if more alarm points are activated, i.e. also max. 5 external LEDs will be turned on.
Analog multi detector | 4300 | 0 | 0.3 | 0 | 0.3 | 0
Analog heat detector | 3308 | 0 | 0.3 | 0 | 0.3 | 0
Analog heat detector, enclosed | 3309 | 0 | 0.2 | 0 | 0.2 | 0
Addressable manual call point | 3333 | 0 | 2 | 0 | 2 | 0
Addressable manual call point, enclosed | 3339 | 0 | 2 | 0 | 2 | 0
Addressable short circuit isolator | 4370 | 0 | 2.2 | 0 | 2.2 | 0 |  | No. of units 0 or 1-8.
Addressable multipurpose I/O unit | 3361 | 0 | 2.2 | 0 | 12 | 0
Addressable siren | 3377 | 0 | 1 | 0 | 13 | 0
Addressable sounder base (low output) | 3378 | 0 | 2 | 0 | 6 | 0
Addressable sounder base (high output) | 3378 | 0 | 2 | 0 | 12 | 0
Addressable 2 voltage outputs unit | 3364 | 0 | 6 | 0 | 6 | 0 |  | ?????????????????strömförbrukningen
External power supply (addressable) | 3366 | 0 | 15 | 0 | 15 | 0
Internal LEDs |  | 0 |  |  | 2 | 0 |  | No. of units is automatically entered. CAN NOT BE CHANGED!
External LED | 2217 | 0 |  | 0 | 1 | 0
Sum. |  | 0 |  | 0 |  | 0 |  | No. of units shall be 0-127. Quiescent sum. and Alarm sum. must be 0-350 mA respectively. Sum mA is depending on cable length / area.
Approx. possible COM loop cable length (m) |  |  |  | 863.2653 |  | 863.2653 |  | The longest cable length to the last unit in any communication direction (A or B direction).
[7 empty] | 863.2653 | NOTE! The shortest cable length is the valid cable length.
Total current consumption quiescent (mA) |  |  |  | 109 |  |  | 16 Ah batt. | Must be < 500 mA when 16 Ah batteries are used. (To fulfil EN54-4.) Must be < 600 mA when 18 Ah batteries are used. (To fulfil EN54-4.)
Total current consumption alarm (mA) | [5 empty] | 125 |  | Must be < 1800 mA.
Battery
Quiescent condition
Required battery backup time (hours) |  | 30 | [5 empty] | HH hours.
Required battery capacity (Ah) |  |  |  | 1.53
Alarm condition
Required battery backup time minutes) |  | 10 | [5 empty] | MM minutes.
Required battery capacity (Ah) | [5 empty] | -0.037167
Totally (quiescent + alarm cond.)
Required battery capacity (Ah) | 1.4928 | [6 empty] | 16 / 18 Ah batteries can be used. The batteries are placed inside the c.i.e.
Information
Total number of COM loop units (addresses) |  | 0
16 Ah batteries can be used
How to write data and get information from the Excel sheet
Data shall be written / edited in the YELLOW cells only.
The Comments column shows help texts for the cell(s) respectively.
Too many units, too long cable length, too high current consumption, etc. will give a warning text.
Useful information / data is shown in the framed cells.
The information in framed cells must not be edited!!
Some cells are filled with color.
Green: Quiescent (normal) condition
Orange: Alarm (activated) condition
Rose: Number of units / cable length
White: Cable length
Light Green: Required battery capacity (Ah)